## Slide 1: Sustainable Reverse Osmosis Water Desalination
Mingheng Li, Professor
Department of Chemical and Materials Engineering
California State Polytechnic University, Pomona
Email: minghengli@cpp.edu
Tel: (909)869-3668

## Slide 2: Outline
Introduction/Background
Optimization of SEC in SWRO
Comparison between SWRO and BWRO
Hydrodynamics and Concentration Polarization
Power Generation by Pressure Retarded Osmosis
An Industrial Case Study

## Slide 3: Section I Introduction/Background

## Slide 4: Industrial Water Desalination
Pretreatment
RO Purification
Post Treatment
Chemical addition
Cartridge filter
RO membrane to remove dissolved solids
CO2 removal, pH adjustment
Disinfection
Distribution
RO is the most versatile industrial technology to produce drinking water, consuming 0.5 kW/m3 and 3.5 kW/m3 energy.

## Slide 5: Reverse Osmosis: How it Works
  Controlled variables:
  permeate rate
  water recovery
  Manipulated variables:
  pump speed
  retentate valve opening ratio
courtesy of M. Busch and J. Johnson, Dow Chemical

## Slide 6: Sustainability Issues in RO
Water recovery can never be close to 100% because of skyrocketing energy consumption required to drive the pump.
In inland areas, any unrecovered water, or brine, is considered as an industrial waste. The brine disposal cost of brackish water RO is approximately $900/mega gallon.
A higher recovery would require a higher energy consumption and/or capital investment in membrane elements.

## Slide 7: Section II Optimization of SEC in Seawater RO (SWRO)
Li, M. Minimization of Energy in Reverse Osmosis Water Desalination Using Constrained Nonlinear Optimization, Industrial & Engineering Chemistry Research, 49, 1822-1831, 2010.
Li, M. Reducing Specific Energy Consumption in Reverse Osmosis (RO) Water Desalination: An Analysis from First Principles, Desalination, 276, 128-135, 2011.
Li, M. Energy Consumption in Spiral-Wound Seawater Reverse Osmosis at the Thermodynamic Limit, Industrial & Engineering Chemistry Research, 53, 3293-3299, 2014.

## Slide 8: Seawater RO Characteristic Equation
=
ΔP –transmembrane hydraulic membrane
Δπ – transmembrane osmotic pressure
Δπ0 – transmembrane osmotic pressure at entrance
Lp – hydraulic permeability
Q – retentate flow rate
Qf – feed flow rate
Qp – permeate flow rate
A – membrane area
Assumptions:
Negligible pressure drop
Negligible concentration polarization
Negligible permeate osmotic pressure
Negligible salt across membrane

## Slide 9: Dimensionless Form
: dimensionless pressure
: recovery
: membrane capacity production ratio
: membrane capacity intake ratio
Coupled relationship among membrane properties, operating parameter and process performance

## Slide 10: Energy Consumption in RO
Specific Energy Consumption
Normalized Specific Energy Consumption
Pump efficiency is usually assumed to be constant for simplified analysis

## Slide 11: Constrained Optimization Model
Contour of NSEC ignoring pump efficiency
Optimization of NSEC
The constrained nonlinear optimization may be solved by various computational tools, e.g., Excel, Matlab (fmincon), Lingo and GAMS etc.

## Slide 12: Optimization Results
NSEC gradually reduces as γ increases.
The lowest NSEC occurs at the thermodynamic limit where driving force is zero.
For single-stage without ERD, as γ →∞, the minimum of NSEC is 4 and the corresponding recovery is 50%.

## Slide 13: Trade-off between Capital Investment and Energy Consumption

## Slide 14: Effect of Staged Operation and ERD
Retentate from a RO stage is pressurized by a booster pump and sent as feed to the next stage.
An energy recovery device (ERD) is used to recover the hydraulic energy of the high pressure brine reject, thus reducing feed pump power consumption.

## Slide 15: Optimization Model

## Slide 16: Optimization Results – without ERD

## Slide 17: Optimization Results – with ERD (ηERD = 90%)

## Slide 18: Optimization Results – with ERD (ηERD = 90%, Ymin = 80%)

## Slide 19: Observations of Optimization Results
A larger allows SWRO to be operated closer to the thermodynamic limit, thus reducing NSEC. However, The NSEC flattens out when becomes sufficiently large.
Using more stages not only reduces NSEC, but also improves overall recovery. The NSEC flattens out when the number of stages increases.
ERD can significantly reduce NSEC, theoretically to 1, while the corresponding recovery approaches 0.
It is possible to obtain an NSEC below 3 while maintaining 80% recovery using all three strategies (e.g., 3-stage, ERD with an efficiency of 90% and a of 2).

## Slide 20: NSEC of RO at Thermodynamic Limit
At thermodynamic limit,
Optimal solution:
NSEC for multi-stage RO with booster pumps and ERD:

## Slide 21: Theoretical Value of NSEC at Thermodynamic Limit
For single- or multi-stage spiral wound RO, the reduction in NSEC due to an ERD at the thermodynamic limit is .
Infinite number of RO stages with booster pumps and a 100% ERD is equivalent to an ideal theoretically reversible RO process, or
Multi-stage design works better at high recoveries. ERD works better at low recoveries.
Brine recirculation would not reduce NSEC.
Without ERD, the minimum of NSEC with infinite stages and inter-stage booster pumps is 3.1462.

## Slide 22: Section III Differences and Similarities between SWRO and BWRO
Li, M. A Unified Model-Based Analysis and Optimization of Specific Energy Consumption in BWRO and SWRO, Industrial & Engineering Chemistry Research, 52, 17241-17248, 2013.

## Slide 23: Difference in Seawater and Groundwater RO
, , , ,
Process model accounting for pressure drop in feed channel

## Slide 24: Plant Design Parameters
Two important parameters show the difference between SWRO and BWRO:
= 390 psi for seawater RO and 10-20 psi for brackish water RO.
Current BWRO plants are not built to have a large .
Effect of retentate pressure drop may not be ignored in BWRO because of a large .
Correlation of and based on literature data from various plants

## Slide 25: Optimization Model
Left: Single- or multi-stage without booster pump
Right: Two-stage (2:1 layout) with booster pump

## Slide 26: Optimization of Single-Stage RO
 |  |  |  |  |  | - | -
BWRO | 0.05 | 1 | 0.059 | 22.9 | 0.75 | 16.1 | 12.7
SWRO | 1 | 0.1 | 0.438 | 4.2 | 0.54 | 1.28 | 0.05
BWRO | 0.05 | 1 | 0.059 | 22.9 | 0.75 | 16.1 | 12.7
SWRO | 1 | 0.1 | 0.438 | 4.2 | 0.54 | 1.28 | 0.05
Pressure drop effect may be ignored in SWRO but not in BWRO.
The optimal recovery for BWRO is much higher mainly because of a smaller .
Operation near thermodynamic limit is only valid for SWRO but not for BWRO.

## Slide 27: Effect of RO Stage Configuration
One stage
Two stage without booster pump
Two stage with booster pump
One stage with brine recirculation

## Slide 28: Optimization Results for Two Cases
= 1 (based on the first-stage in a two-stage RO)
= 0.1 (based on the first-stage in a two-stage RO)

## Slide 29: Observations of Optimization Results
For BWRO, single-stage is better than two-stage in terms of NSEC (However, industrial design employs two-stage to achieve a more uniform flow). Using booster pump does not improve NSEC under optimal conditions because of a very small .
For SWRO, two-stage with booster pump could be better than one-stage in terms of NSEC if is sufficiently large. Using booster pump does improve NSEC under optimal conditions.
Brine recirculation does not improve NSEC in BWRO due to increase in feed salinity and retentate pressure drop.

## Slide 30: Section IV Hydrodynamics and Concentration Polarization in Industrial RO Feed Channel
Li, M. Three-Dimensional CFD Analysis of Hydrodynamics and Concentration Polarization in an Industrial RO Feed Channel, in review.

## Slide 31: Concentration Polarization
Concentration Polarization Modulus:
Mass transfer boundary layer in narrow flat channel:
It is discussed extensively in literature that concentration polarization has a strong adverse effect on water flux. However, we argue that its effect may not be so significant in commercial RO under realistic industrial operating conditions.

## Slide 32: Commercial RO Feed Channel with Spacer Filaments
courtesy of M. Busch and J. Johnson, Dow Chemical
Geometry construction using COMSOL
Spiral wound RO feed spacer

## Slide 33: Comparison between Flat and Spacer-Filled Channels

## Slide 34: Comparison of Mass Transfer between Flat and Spacer-Filled Channels

## Slide 35: Observations of the Effect of Feed Spacer Filaments
The pressure drop v.s. average longitudinal velocity can be approximated by and the trend matches an empirical correlation previously derived from plant data.
Substantial wall-parallel velocity near the membrane surface is observed, which helps suppress boundary layer development. Rolling cells are formed in the center of the feed channel, which promote transverse mixing.
Different from concentration polarization phenomenon in flat, narrow channels, concentrated islands are isolated in regions near spacer filaments where flow is relatively stagnant. The local mass transfer coefficient oscillates. longitudinally but the cell-average appears fairly constant in cells adjacent to each other. It is shown that under plant operating conditions.
Concentration polarization is not very significant in modeling industrial BRWO.

## Slide 36: Section V Power Generation from Seawater or SWRO Brine by Pressure Retarded Osmosis
Li, M. Analysis and Optimization of Pressure Retarded Osmosis for Power Generation, AIChE Journal, 61, 1233-1241, 2015.

## Slide 37: Pressure Retarded Osmosis
PRO may be used to generate power from seawater or brine from SWRO.
There are discussions in literature about integration of PRO with RO to reduce the energy consumption of RO.
Flux: is usually assumed to be constant in literature, which may not be true.
Power Density:
Maximum occurs at based on literature.

## Slide 38: Basic Definitions in PRO
Specific Energy Production (SEP)
= =
: dilution ratio at the end of the membrane
: applied pressure
Normalized SEP or Osmotic to Hydraulic Efficiency
= = =
Power Density (PD)

## Slide 39: Characteristic Equation without Concentration Polarization
Local water flux (assuming ):
Dimensionless form:
, , and
Solution:
qd: dilution ratio at the end of the membrane

## Slide 40: Optimization of NSEP
Optimization of NSEP:
Observations from profiles of and NSEP
increases as reduces and/or increases.
At a fixed , there is an optimal corresponding the maximum NSEP.

## Slide 41: Optimization Results
Observations:
The optimal shifts away from as increases.
An increase in () significantly reduces and NSEP.
When (or fresh water is used as feed solution), the largest NSEP occurs at forward osmosis conditions, i.e., = 0.

## Slide 42: Optimal Driving Force in PRO
Similarities between RO and PRO
  A larger allows the PRO to be operated closer to its thermodynamic limit, thus improving SEP.
  A larger allows the RO to be operated closer to its thermodynamic limit, thus improving SEC.

## Slide 43: Optimization of PRO Accounting for Concentration Polarization
is in an implicit form.

## Slide 44: Short-Cut Optimization Method
If and , may be approximated by where and .
The characteristic equation becomes , where .
Optimization model:
Note:
It is found that this method provides very accurate solution to . However, flux profile, NSEP and PD are better calculated using the original concentration polarization model and the derived .

## Slide 45: Optimization Results
Parameters are taken from literature (Achilli, JMS, 2009)
Comparison between short-cut and rigorous optimization methods (values obtained using the short-cut optimization method, if different from the rigorous method, are presented in parenthesis):
= 2763 kPa | , kPa | , m/s | PD, W/m2 |  |  | , %
= | 1330 (1316) | 2.16 (2.18) | 2.87 | - | - | -
m/s | 1300 (1295) | 1.78 (1.79) | 2.31 | 0.65 | 1.22 | 10.5
m/s | 1260 (1259) | 1.56 (1.56) | 1.96 | 1.29 | 1.39 | 17.7
m/s | 1190 (1186) | 1.28 (1.28) | 1.52 | 2.58 | 1.64 | 27.6
m/s | 1070 (1067) | 1.00 (1.01) | 1.07 | 5.17 | 2.01 | 38.9
= 2763 kPa | , kPa | , m/s | PD, W/m2 |  |  | , %
= | 2390 (2325) | 3.38 (3.47) | 8.07 | - | - | -
m/s | 2260 (2244) | 2.64 (2.66) | 5.97 | 1.14 | 1.33 | 15.3
m/s | 2140 (2133) | 2.24 (2.25) | 4.79 | 2.28 | 1.56 | 24.6
m/s | 1950 (1943) | 1.79 (1.80) | 3.50 | 4.56 | 1.90 | 35.8
m/s | 1680 (1685) | 1.38 (1.38) | 2.32 | 9.13 | 2.37 | 47.4
 |  |  | PD, W/m2 |  |  | 
 | 1330 (1316) | 2.16 (2.18) | 2.87 | - | - | -
 | 1300 (1295) | 1.78 (1.79) | 2.31 | 0.65 | 1.22 | 10.5
 | 1260 (1259) | 1.56 (1.56) | 1.96 | 1.29 | 1.39 | 17.7
 | 1190 (1186) | 1.28 (1.28) | 1.52 | 2.58 | 1.64 | 27.6
 | 1070 (1067) | 1.00 (1.01) | 1.07 | 5.17 | 2.01 | 38.9
 |  |  | PD, W/m2 |  |  | 
 | 2390 (2325) | 3.38 (3.47) | 8.07 | - | - | -
 | 2260 (2244) | 2.64 (2.66) | 5.97 | 1.14 | 1.33 | 15.3
 | 2140 (2133) | 2.24 (2.25) | 4.79 | 2.28 | 1.56 | 24.6
 | 1950 (1943) | 1.79 (1.80) | 3.50 | 4.56 | 1.90 | 35.8
 | 1680 (1685) | 1.38 (1.38) | 2.32 | 9.13 | 2.37 | 47.4
Parameters | Value
 | 8.48 m/s
 | 4.51 s/m
 | 1.11 m/s
 | 1.87 m/s/kPa
 | 2763, 4882 kPa
Parameters | Value
 | 2763, 4882 kPa

## Slide 46: Power Density and Flux Profile
Six cases:
Black: no CP.
Red: with CP.
Magenta: m/s.
Yellow: m/s.
Blue: m/s.
Green: m/s.

## Slide 47: Conclusions from PRO Optimization
Short-cut optimization yields essentially the same solution as the rigorous solution. Moreover, it provides parameters to explain the effect of ICP, ECP and dilution in DS.
Shift of optimal from :
  Dilution effect (i.e. is not zero).
  Internal concentration polarization (i.e., ).
Nonlinearities and conflicting power density and efficiency in process scale-up
  Realistically, up to 25% of the osmotic energy in SWRO brine may be recovered if similar membranes are invested in PRO (i.e., the capital investment in RO elements will be doubled).

## Slide 48: Section VI An Industrial Case Study
Li, M.; Noh, B. Validation of Model-Based Optimization of Brackish Water Reverse Osmosis (BWRO) Plant Operation, Desalination, 304, 20-24, 2012.
Li, M. Optimization of Multitrain Brackish Water Reverse Osmosis (BWRO) Desalination, Industrial & Engineering Chemistry Research, 51, 3732–3739, 2012.
Li, M. Optimal Plant Operation of Brackish Water Reverse Osmosis (BWRO) Desalination, Desalination, 293, 61-68, 2012.

## Slide 49: Chino I Desalter
Draws raw water from 15 groundwater wells
Processes 14 MGD of drinking water
1.7 megawatt (0.5 megawatt is for RO)
Serves the Chino basin and neighboring areas
VOC
RO
2 MGD
7 MGD
5 MGD
Ion Exchange
Wells 1- 4
Wells 5- 15
Final Blended Product
14 MGD
Product Quality Requirement
TDS: 350 mg/L
Nitrate: 25 mg/L

## Slide 50: Desalination RO Unit
Consists of 4 process trains, each equipped with:
  a dedicated membrane feed pump with VFD – 9 stage vertical turbine pump with 300 hp motor, 1450 gpm, 625 ft TDH at 1785 rpm

## Slide 51: RO Stage Configuration and Layout
  Two-stage pressure vessel array (28+14)x7 = 294 RO elements
  No inter-stage booster pump

## Slide 52: Typical Brackish Feedwater Analysis
Parameter | Value
Calcium (Ca), mg/L | 174
Magnesium (Mg), mg/L | 40
Sodium (Na), mg/L | 48
Potassium (K), mg/L | 3
Carbonate (as CO3), mg/L | 0
Bicarbonate (as HCO3), mg/L | 490
Sulfate (SO4), mg/L | 55
Chloride (Cl), mg/L | 102
Nitrate (as NO3), mg/L | 170
Silica (as SiO2), mg/L | 37
Barium (Ba), mg/L | 0.20
Fluoride (F), mg/L | 0.20
Strontium (Sr), mg/L | 1.3
Total Dissolved Solids (TDS), mg/L | 924
pH, units | 6.5
Temperature, degrees C | 20

## Slide 53
k – pressure drop factor
ΔP –pressure difference across the membrane
Po – feed pressure prior to pump
ΔPpump – pressure increase across pump
Pp – permeate pressure
Q – retentate flow rate
Qf – feed flow rate
Δπo – osmotic pressure change across the membrane entrance
RO Process Model

## Slide 54
Parameter | Value
Number of pressure vessels per train | 42
Number of 1st stage pressure vessels | 28
Number of 2nd stage pressure vessels | 14
Number of membrane elements per vessel | 7
Area per element, ft2 | 400
Feed pressure, , psi | 40.6
Feed osmotic pressure, , psi | 9
Feed flow, , gpm | 1,525
Permeate pressure, , psi | 16.4
Permeate flow, , gpm | 1,234
Recovery, , % | 80.9
Retentate pressure drop in 1st stage, , psi | 24.9
Retentate pressure drop in 2nd stage, , psi | 18.2
Pump head, , ft | 360
Parameter | Value
Number of pressure vessels per train | 42
Number of 1st stage pressure vessels | 28
Number of 2nd stage pressure vessels | 14
Number of membrane elements per vessel | 7
Area per element, ft2 | 400
 | 40.6
 | 9
 | 1,525
 | 16.4
 | 1,234
 | 80.9
 | 24.9
 | 18.2
 | 360
Plant Production Data – Train 1

## Slide 55: Parameter Identification from Plant Operation Data
k = 2.1×10-5 psi/gpm2 (in the first stage)
Lp = 0.11 gfd/psi

## Slide 56: Optimization Model

## Slide 57: RO Plant Trial Methodology
Data was taken from Train 1 over 4 days
Permeate flow rate kept constant at 1235 GPM
Recovery rate was varied from 78 to 95% and the resulting field data were recorded for analysis

## Slide 58
Quality of Feedwater
Pump Speed
(92% of 1785 rpm)
Pump Output
RO Input
Retentate Valve Position
Retentate Flowrate
Permeate Flowrate
Quality of Permeate

## Slide 59: Plant Validation of Model

## Slide 60: Improved model incorporating CFD results

## Slide 61: Optimization of Multi-train RO
A desalination plant may have multiple RO trains with RO elements of different service times.
Older membranes tend to have lower Lp.
By optimally allocating permeate production rates among all trains based on Lp, the SEC of the whole plant may be reduced.

## Slide 62: Economic Considerations for Sustainable Production
Model predicts optimum recovery point
  Power saving ($40 K/year)
  Reduction in brine volume (>50%) which leads to less disposal cost ($ 360 K/year)
  Faster membrane fouling not quantified ($ negative)
Requires comprehensive optimization study prior to implementation
Precipitation in Brine Line after 13 Years of Service

## Slide 63: Related Publications
Li, M. Three-Dimensional CFD Analysis of Hydrodynamics and Concentration Polarization in an Industrial RO Feed Channel, in review.
Li, M. Analysis and Optimization of Pressure Retarded Osmosis for Power Generation, AIChE Journal, 61, 1233-1241, 2015.
Li, M. Energy Consumption in Spiral-Wound Seawater Reverse Osmosis at the Thermodynamic Limit, Industrial & Engineering Chemistry Research, 53, 3293-3299, 2014.
Li, M. A Unified Model-Based Analysis and Optimization of Specific Energy Consumption in BWRO and SWRO, Industrial & Engineering Chemistry Research, 52, 17241-17248, 2013.
Li, M.; Noh, B. Validation of Model-Based Optimization of Brackish Water Reverse Osmosis (BWRO) Plant Operation, Desalination, 304, 20-24, 2012.
Li, M. Optimization of Multitrain Brackish Water Reverse Osmosis (BWRO) Desalination, Industrial & Engineering Chemistry Research, 51, 3732–3739, 2012.
Li, M. Optimal Plant Operation of Brackish Water Reverse Osmosis (BWRO) Desalination, Desalination, 293, 61-68, 2012.
Li, M. Reducing Specific Energy Consumption in Reverse Osmosis (RO) Water Desalination: An Analysis from First Principles, Desalination, 276, 128-135, 2011.
Li, M. Minimization of Energy in Reverse Osmosis Water Desalination Using Constrained Nonlinear Optimization, Industrial & Engineering Chemistry Research, 49, 1822-1831, 2010.

## Slide 64: Acknowledgements
Students Brian Noh, Sophia Bui and Steven Chao helped the development of this module.