Contents

1 Introduction	1-14

Motivation	1-14

Coal to Electricity	1-15

Summary	1-16

2 Description of the Power Plant Model	2-1

Introduction	2-1

Process Description	2-1

Boiler	2-5

Steam Cycle	2-6

ASPEN Sections	2-9

ASPEN Unit Operations	2-9

ASPEN Streams	2-9

ASPEN Design Specification & Convergence Blocks	2-31

ASPEN Calculator Blocks	2-37

ASPEN Computational Sequence	2-40

Summary	2-44

3 Summary	3-1

A References	A-1

List of Figures

Figure 1-1 Total World Electricity Generation by Fuel (2006)	1-14

Figure 1-2 Electricity Generation from Coal	1-15

Figure 2-1 Process Flow Diagram of a Coal Powered Supercritical Power Plant	2-2

List of Tables

Table 1-1 Contribution of Coal towards Electricity Production	1-14

Table 2-1 List of Components	2-3

Table 2-2 Analysis of various components	2-4

Table 2-3 Stream Table for the streams in Figure 2-1	2-5

Table 2-4 Details of Input Streams	2-11

Table 2-5 Unit Operations and Mass Streams	2-13

Table 2-6 Unit Operations with Energy Streams	2-24

Table 2-7 Unit Operations with Work Streams	2-28

Table 2-8 List of Design Sepcifications	2-33

Table 2-9 List of Convergences	2-37

Table 2-10 List of Calculators	2-38

Table 2-11 Sequencing of the Boiler Section	2-40

Table 2-12 Sequencing of the Steam Cycle Section	2-41

# Introduction

Motivation

Coal-fired power plants are the largest source of CO2 emissions. However, coal also plays a crucial role in electricity generation worldwide. Figure 1-1 shows the total world electricity generation by fuel type. From this figure, it can be seen that 41% of the global electricity is produced by coal-fired power plants.

Figure 1-1
Total World Electricity Generation by Fuel (2006) [1]

The dependence on coal for the production of electricity is common throughout the world. Table 1-1 shows the contribution of coal towards the total electricity production in various countries of the world.

Table 1-1
Contribution of Coal towards Electricity Production [1]

| Country | % Contri | Country | % Contri | Country | % Contri | Country | % Contri |
| --- | --- | --- | --- | --- | --- | --- | --- |
| South Africa | 94% | Australia | 76% | India | 68% | Greece | 55% |
| Poland | 93% | Israel | 71% | Czech Rep | 62% | USA | 49% |
| PR China | 81% | Kazakhstan | 70% | Morocco | 57% | Germany | 49% |

From Table 1-1, it can be seen that in some countries like Poland and South Africa the contribution of coal towards electricity generation is more than 90% of the total electricity generated. This table also highlights the fact that despite CO2 emissions, humanity cannot live comfortably without coal power plants. This trend has been predicted to only increase despite the diminishing of coal resources. A study [1] shows that almost 44% of global electricity produced in 2030 will be coal based. In United States, 49% of the electricity produced is attributed to the combustion of coal in coal-fired power plants. The fact that US has the highest proved recoverable coal reserves [2] in the world also makes the coal-fired power plants imperative in US. The reserve life for the coal in US has been predicted to be 234 years and thus coal-fired power plants will continue to exist for a considerable period of time in future.

A considerable research effort is directed towards increasing the efficiency of these power plants so that they are environmentally sustainable by emitting lesser CO2. A one percentage point improvement in the efficiency of a conventional pulverised coal combustion plant has been reported to decrease the CO2 emissions by almost 2-3% [1].

Coal to Electricity

The generation of electricity from coal is shown in Figure 1-2 and a brief description is discussed [1]: The initial step is to mill the coal to a fine powder. This procedure helps in increasing the surface area and subsequently allows the coal to burn more quickly. The powdered coal is blown into the combustion chamber of a boiler with the help of atmospheric air where it is burnt at high temperature. The hot gases and heat energy produced due to the combustion of coal is used to convert water into steam within the tubes lining the boiler.

Figure 1-2
Electricity Generation from Coal [1]

The high pressure steam produced by the combustion of coal is passed into a turbine containing thousands of propeller-like blades. The steam does mechanical work by pushing these blades causing the turbine shaft to rotate at high speed. A generator is mounted at one end of the turbine shaft and consists of carefully wound wire coils. Electricity is generated when these are rapidly rotated in a strong magnetic field. After passing through the turbine, the steam is condensed and returned to the boiler to be heated once again thereby forming a recycle loop. The electricity is transmitted to the grid which subsequently caters to the various requirements of the ecosystem.

Summary

The importance of coal power plants has been briefly discussed in this chapter. In the next chapter of this report, we will develop a ASPEN model of a coal based power plant which can be used in the study and comparison of different environmental control technologies.

# Description of the Power Plant Model

Introduction

In the previous chapter, we have discussed the importance of coal-fired power plants in producing electricity and also mentioned briefly about working of a power plant. In this chapter, we will provide details of a pulverized coal-fired power plant built in ASPEN. The model is based on a super critical steam cycle and uses air for the combustion of coal. We will begin this chapter by providing a brief description of the ASPEN model and subsequently discuss the various components of the ASPEN model. A recent NETL report [3] discusses in detail various configurations of power plants including coal based sub and super critical power plants. This report has been extensively used in the building of the model reported in this chapter.

Process Description

The brief description presented in this section is based on the block flow diagram shown in Figure 2-3 and also the stream numbers referenced correspond to this figure. Detailed information including cost estimation on the various unit operations can be obtained from literature [3].

Coal (stream 6) and primary air (stream 4) are fed into the boiler through the wall-fired burners. Forced draft fans are employed to provide additional combustion air (stream 2), including the over-fire air. There is an air leakage into the boiler as it is operated at a slight negative pressure. This infiltration air is accounted by the stream 5.

The flue gas from the combustion exits the boiler through the SCR reactor (stream 8) and is cooled to 177°C (350°F) in a combustion air preheater. This is subsequently passed through a fabric filter for the removal of particulate substances (stream 10). An ID fan is used to increase the flue gas temperature to 188°C (370°F) and provides the motive force for the flue gas (stream 11) to pass through the FGD unit.

The input streams into the FGD are makeup water (stream 13), oxidation air (stream 14), limestone slurry (stream 12) and the output product from FGD is gypsum (stream 15). The clean, saturated flue gas exiting the FGD unit (stream 16) passes to the plant stack and can be discharged to atmosphere.

Table 2-2 shows the list of 20 components used in the ASPEN plus model.  Although, mercury is released when coal is burnt, it is considered trace element and is not included directly in the flowsheet development because it is released in atmosphere. For Illinois no. 6, the mercury content is 0.09±0.06 parts per million of coal on dry basis. Mercury release can be calculated directly from this data.  There are nine conventional streams, another nine components modeled as solids and two components modeled as non conventional substances. Table 2-3 shows the detailed component analysis of coal, air and limestone. Table 2-4 provides the process data for the numbered streams in the flow diagram.

Figure 2-3
Process Flow Diagram of a Coal Powered Supercritical Power Plant [3]

Table 2-2
List of Components

|  | COMPONENT ID | TYPE | COMPONENT NAME | FORMULA |
| --- | --- | --- | --- | --- |
| 1 | H2O | Conventional | Water | H2O |
| 2 | AR | Conventional | Argon | AR |
| 3 | CO2 | Conventional | Carbon-Dioxide | CO2 |
| 4 | O2 | Conventional | Oxygen | O2 |
| 5 | N2 | Conventional | Nitrogen | N2 |
| 6 | O2S | Conventional | Sulfur-Dioxide | O2S |
| 7 | H2 | Conventional | Hydrogen | H2 |
| 8 | SO2 | Conventional | Sulfur-Dioxide | O2S |
| 9 | SO3 | Conventional | Sulfur-Trioxide | O3S |
| 10 | CASO4 | Solid | Calcium-Sulphate | CASO4 |
| 11 | C | Solid | Carbon-Graphite | C |
| 12 | CACO3 | Solid | Calcium-Carbonate-Aragonite | CACAO3-A |
| 13 | CAO | Solid | Calcium-Oxide | CAO |
| 14 | INERT | Solid | Silicon-Dioxide | SIO2 |
| 15 | MGCO3 | Solid | Magnesium-Carbonate | MGCO3 |
| 16 | MGO | Solid | Magnesium-Oxide | MGO |
| 17 | S | Solid | Sulfur | S |
| 18 | GYPSUM | Solid | Calcium-Sulfate-Dihydrate-Gypsum | CASO4*2H2O |
| 19 | RAWCOAL | NC |  |  |
| 20 | ASH | NC |  |  |

Table 2-3
Analysis of various components

|  | ANALYSIS | Element | Value |
| --- | --- | --- | --- |
| Illinois #6 Coal (in terms of %) | Coal Ultimate Analysis (Dry Basis) | ASH | 10.91 |
|  |  | CARBON | 71.72 |
|  |  | HYDROGEN | 5.06 |
|  |  | NITROGEN | 1.74 |
|  |  | CHLORINE | 0 |
|  |  | SULFUR | 2.82 |
|  |  | OXYGEN | 7.75 |
|  | Coal Proximate Analysis (Dry Basis) | MOISTURE | 11.12 |
|  |  | FIXED CARBON | 49.72 |
|  |  | VOLATILE MATTER | 39.37 |
|  |  | ASH | 10.91 |
|  | Coal Sulfur Analysis | PYRITIC | 2.82 |
|  |  | SULFATE | 0 |
|  |  | ORGANIC | 2.82 |
| Air (in terms of mass fraction) | H2O |  | 0.00616201 |
|  | AR |  | 0.01280219 |
|  | CO2 |  | 0.0004983 |
|  | O2 |  | 0.2299842 |
|  | N2 |  | 0.7505533 |
| Limestone (in terms of mass fraction) | CACO3 |  | 0.804 |
|  | INERT |  | 0.161 |
|  | MGCO3 |  | 0.035 |

Table 2-4
Stream Table for the streams in Figure 2-3 [3]

Boiler

The amount of coal required depends on the quantity of power to be produced by the power plant and is determined using the design specification D-ST-COA. This design specification manipulates the flowrate of the stream COAL so that the heat streams QSTEAM and Q-STMTOT are equal or below the specified tolerance. The coal entering the power plant is disassembled into its constituent atoms/molecules using a RYIELD block (DECOM). A calculator block (C-DECOMP) is executed before the DECOM block which disassembles the coal into its constituent molecules/atoms based on the ultimate analysis.

The amount of air required for combustion depends on the amount of coal determined by the above mentioned design specification. Once the amount of coal is fixed, the amount of air required is determined by the calculator C-AIR-IN. This calculator determines the flowrate of primary air P-AIR through the compressor PRIAIR, the secondary air S-AIR through the compressor SECAIR and the infiltration air LEAK-AIR into the mixer BOIL-MX. The primary and secondary air is compressed from atmospheric pressure to approximately over 15 psia. The primary air is to model the air that blows the coal to the PC boiler while the secondary air models the remaining air that is added to the boiler. The infiltration air is to model the air leakage into the boiler and is 1.5% of the total air inlet.

The three air streams and the coal stream are mixed in a mixer BOIL-MX before being fed to the boiler (BOILER). The boiler is modeled as an RSTOIC block and is set to operate at a pressure of 14.01 psia and a temperature of 270°F. The boiler models the combustion reactions and the heat duty is set to match that of the steam turbine by design specification and the heat lost calculated by QLOSS.

The ash removal is modeled separately in a FLASH2 block named ASHREM. The ash separation is not modeled in the boiler as the number of outlet streams is limited to one (plus a water outlet) in the ASPEN block RSTOIC. The combusted coal is fed to the ASHREM block which removes 20% of the solid ash in the feed. The stream exiting the ash separator is fed into BAGHSE. This block is also modeled as a flash drum and removes the remaining ash and particulates from the stream exiting the ash separator, However, a pressure drop of ~ 0.2 psi is incurred in this unit operation. This stream is fed to PCOMP which has an isentropic efficiency of 65%  and helps in returning the baghouse outlet stream to a pressure of 15 psi.

Slurry of limestone is prepared by mixing limestone (RAWLIME) and water (LIME-H2O) in the LIM-MIX mixer. The amount of limestone is determined by the design specification D-FGDLIM based on the SO2 content of the flue gas entering the FGD unit. The flowrate of limestone is manipulated such that the CaCO3/SO2 ratio is 1.04. The amount of water required (LIME-H2O) for the preparation of this slurry is determined by the design specification D-FGDSOL. The amount of water is manipulated such that the slurry mixture is 30% solids. This slurry is pumped by the slurry pump LIM-PUMP to the mixer FGD-MIX where it is mixed with the air required for the FGD operation. The amount of air required is determined by the design specification D-FGD-O2. The amount of air is manipulated so that the ratio of O2/SO2 is 1.1.

The limestone slurry along with the air required for FGD then enters the FGD. The FGD is modeled as an RSTOIC unit in which 98% of the SO2 is reacted to form CO2 and gypsum. The resulting product form the FGD is fed into the gypsum separator GYM-REM. This unit is modeled as a flash drum and serves the purpose of separating gypsum, MgCO3, CaCO3, and inert materials from the FGD outlet stream. The gypsum stream then combines with the make-up water feed. The effluent stream from the gypsum separator, which contains concentrated CO2 is sent to the stack in the absence of a carbon capture system.

Steam Cycle

The steam cycle can be considered to be composed of two parts: the heating of feedwater to produce steam and the subsequent work done by the generated steam to produce power. The resulting steam after the production of power is condensed and again used as feedwater thereby comprising a recycle loop. The heating of feedwater is usually done by the help of steam extracted during the production of power. A brief description of each of these two parts is presented below.

The production of power by steam is realized by passing the steam through a High Pressure Turbine (HPT), a Medium Pressure Turbine (MPT) and a Low Pressure Turbine (LPT) section. The steam enters through the HPT section followed by the MPT section and finally leaves through the LPT section to the condenser. All these sections are connected to the generator by using a common shaft. The HPT section is modeled as a three stage turbine comprised of HPT-GOV, HPT-1 and HPT-2. The MPT section is modeled as a two stage turbine comprised of MPT-1 and MPT-2 whereas the LPT section is modeled as five stage turbine comprised of LPT-1,LPT-2, LPT-3,LPT-4, and LPT-5. The outlet pressures and isentropic efficiencies are specified for each of these ten stages.

The steam enters the turbine HPT-GOV at a pressure of 3500 psig and temperature of 1110°F through the control valves. The amount of steam entering the steam cycle depends on the power output of the plant and is determined using the design specification D-PWROUT. The steam leaves the final HPT stage (HPT-2) at a pressure of 710.8 psia. The steam is split before entering and after leaving the first stage of the HPT section expansion to account for valve stem and shaft leakages. This is implemented by specifying the amount of flow in the block input. A portion of the steam is extracted (2-VLV-1) between the turbines HPT1 and HPT2 to heat the feedwater via the heater H1B. The amount of steam to be extracted is determined by the design specification D-H1. The remaining portion of the steam enters the final HPT turbine (HPT-2). A portion of the steam leaving HPT-2 is again extracted for heating the feedwater in the heater H2B. The exact amount of steam extracted is determined by the design specification (D-H2). After this second extraction, the remaining steam is reheated in a reheater (RE-HEAT). A subsequent heater REHT-LOS is used to account for the heat and pressure losses.

The steam enters the IP turbine section at a pressure of 654 psia and a temperature of 1150°F. In between the first and second IP turbine stages (i.e., MPT-1 and MPT-2), a portion of the steam is extracted for heating the feedwater via H3B. After this extraction, steam enters MPT-2 and leaves the second stage of the turbine at a pressure of 137.7 psia and a temperature of 717°F. A portion (2-MXR-4) of this leaving stream is mixed with the feedwater in the deaerator (H4-DEA). The amount of steam to be extracted after the MPT-1 and MPT-2 turbines is controlled by design specifications D-H3 and D-H4.

The steam leaving the second stage (MPT-2) of the MPT section is split into two. One of these streams is fed to the boiler feedwater turbine (FW-TRB) while the other stream enters the LPT section at a pressure and temperature of 123 psig and 717°F respectively.  The steam flows through the LPT section and is finally condensed in the condenser at 0.9823 psia. The split for the boiler feedwater turbine (2-FW-TRB) is controlled by design specification D-BFW. A total of four steam extractions are modeled in the LPT turbine section, in between each of the five stages. The amount of steam to be extracted is determined by the design specifications D-H5,D-H6,D-H7 and D-H8. These four extracted steam are used in heating the feedwater using the heaters H5B,H6B,H7B and H8B.

The total work done by each of the ten turbines is calculated in the work mixer W-SUMMER block and includes the work lost in the turbines. The block WORKLOSS is used to model the generator losses and the final work done by the steam is indicated by the work stream W-NET. This completes one part of the steam cycle i.e., the production of power using steam. We will now briefly discuss the second part of the steam cycle which involves the heating of the feedwater.

The feedwater used in the feedwater heating system is the expanded steam that enters the condenser block (COND). The condenser is modeled to bring all water entering it to a saturated liquid at 0.9823 psia. This block is also the point at which steam cycle makeup water (MU-COND) under atmospheric conditions (60°F and 14.7 psia) is brought into the plant. The condensate is subsequently pumped to 100 psia using CON-PUMP and some heat from turbine steam losses is recovered before process heat is recovered from steam cooling.

The drained steam from the condenser (or the feedwater) is heated by a series of seven feedwater heaters (excluding the deaerator). The feedwater heaters are implemented by using two single-sided heaters each, representing the steam side and the feedwater side. For example, H8 and H8B is one such pair of heater comprising a single heat exchanger. The other six pairs are H7-H7B, H6-H6B, H5-H5B, H3-H3B, H2-H2B, H1-H1B. The outlet stream temperature from the heaters H8 to H1 are calculated by calculators C-H8 to C-H1 respectively whereas the temperatures of the heaters H8B to H1B are determined by the calculators C-H8B to C-H1B respectively. The design specifications D-H1 to D-H8 extract an appropriate amount of steam from the turbines such that the heat gained by the feedwater is equal to the heat lost by the condensing steam. For example the heat gained in H8 should be the same as that of the heat lost in H8B. In other words, Q-H8 should be zero or below some specified tolerance. Such a strategy is implemented for all the other six pairs of heat exchangers.

The steam side releases heat by condensing the extracted steam from the turbines. The condensate leaves as the drain stream for the feedwater heater system. The drain temperature is set based on the specified degrees of drain or subcooling and the temperature of the inlet feedwater (inlet to feedwater side). The drain from a preceding heat exchanger is mixed with the steam extracted in the subsequent heat exchanger. For example, the drain (DR1) from the heater H1B is mixed with the steam extracted (2-H2B) in the heater H2B. This strategy is implemented for all the steam side heat exchangers. However, an exception being the drain (DR3) from the heat exchanger H3B which is mixed with the steam extracted (2-H4B) and is combined in the deaerator with the feedwater instead of being sent to the heater (H5B).

The heaters on the feedwater side heats the inlet feedwater based on a specified terminal temperature difference and the saturation temperature of the extraction steam entering the feedwater heater system (inlet to steam side). The feedwater (BW-6) from the heater H5 is combined with the drain DR3 from the heater H3B and the steam extracted from MPT-2 in the deaerator. This combined stream leaving the deaerator is pumped to 4200 psia by the boiler feedwater pump (FW-PUMP). This allows for the pressure drop across the feedwater heaters and ensures that the throttle steam pressure requirement is satisfied. This stream is subsequently heated in the remaining three heaters H1 through H3.

The pressurized stream enters the superheater (SUP-HEAT) at a pressure of 4185 psia and a temperature of 557°F. The superheater increases the steam temperature to 1155°F, while the pressure decreases through the superheater to 3600 psia. The heater block (STM-LOSS) is modeled to account for the temperature and pressure losses in the superheater. It reduces the temperature by 5°F and pressure by approximately 85 psi to produce throttle steam at a pressure of 3514.7 psia and a temperature of 1110°F. The heat required for the superheater and the reheater is provided by the BOILER in the Boiler section. This completes the description of the steam cycle and the complete flowsheet

The following components of the ASPEN model are discussed in detail

- Sections

- Streams

- Blocks

- Design Specifications

- Convergences

- Calculators

- Sequences

ASPEN Sections

The flowsheet is divided into two sections namely the boiler section (ASPEN ID: SEC-BIOL) and steam cycle (ASPEN ID: SEC-SC). The section SEC-BIOL consists of all the unit operations required to model the combustion of coal whereas the section SEC-SC consists of all the unit operations required to model the steam cycle. The IDEAL property method is used for the boiler section whereas the STEAM-TA is used as property method for the steam cycle. There is no mass stream interacting between these two sections. The only interaction between these two streams is an energy stream which uses the heat from the boiler to produce steam.

ASPEN Unit Operations

The ASPEN model consists of a total of unit 82 unit operations. The boiler section has 16 of these unit operations whereas the steam section has the remaining 66 unit operations. A detailed list of these unit operations is given in Table 2-6. This table provides the use of each of the 82 unit operations along with its ASPEN ID and the ASPEN PLUS unit used to model the particular unit operation. In addition, the table also gives the input and output streams entering and leaving each of this unit operation. Apart from the unit operations mentioned in this table, there are also energy and work mixers/splitters which are presented in Table 2-7.

ASPEN Streams

There are three type of streams namely the mass streams, the energy streams and the work streams. There are a total of 171 streams. Of these, there are 115 mass streams, 35 energy streams and 21 work streams. The details of the mass streams can be obtained from the Table 2-6. The complete details of the energy streams are given in Table 2-7 whereas the details of the work streams are given in Table 2-8.

Table 2-5
Details of Input Streams

| Sl. No. | Stream | ASPEN ID | Flowrate | Temp | Pressure | Composition Mole % |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Primary Air for combustion | P-AIR | Calculated using calculator C-AIR-IN | 590 F | 14.7 psia | Refer Air in Table 2-3 |
| 2 | Secondary for combustion Air | S-AIR | Calculated using C-AIR-IN | 590 F | 14.7 psia | Refer Air in Table 2-3 |
| 3 | Leakage Air in Boiler | LEAK-AIR | Calculated using C-AIR-IN | 590 F | 14.7 psia | Refer Air in Table 2-3 |
| 4 | Coal feed for combustion | COAL | Calculated using the design specification D-ST-COA | 590 F | 14.7 psia | Refer Coal in Table 2-3 |
| 5 | Limestone feed for FGD | RAWLIME | Calculated using the design specification D-FGDLIM | 590 F | 14.7 psia | Refer Limestone in Table 2-3 |
| 6 | Limestone slurry water | LIME-H2O | Calculated using the design specification D-FGDSOL | 590 F | 14.7 psia | 100% water |
| 7 | Water for FGD | H2O-FGD | Calculated using C-FGDWAT | 590 F | 14.7 psia | 100% water |
| 8 | Oxidation air for FGD | FGD-AIR | Calculated using the design specification D-FGD-O2 | 590 F | 14.7 psia | Refer Air in Table 2-3 |
| 9 | Make-up water for FGD | MUP-H2O | Calculated using C-FGDWAT | 590 F | 14.7 psia | 100% water |
| 10 | Steam Inlet for HP turbine | STEAM | Calculated using the design specification D-PWROUT | 11100 F | 14.7 psia | 100% water |
| 11 | Make-up water for condenser | MU-COND | Specify to be zero | 600 F | 14.7 psia | 100% water |
| 12 | Exit loss from steam turbine | W-TURLOSS | Specify to be 10000 hp | N/A | N/A | N/A |

Table 2-6
Unit Operations and Mass Streams

| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| BOILER SECTION |  |  |  |  |  |  |  |
| 1 | Coal feed for the power plant | COAL | Decomposition of coal into individual components | DECOM | RYield | COALCOMP | Decomposed coal |
| 2 | Primary air for the combustion | P-AIR | Primary air compression | PRIAIR | Compressor | P-AIR-C | Compressed primary air |
| 3 | Secondary air for the combustion | S-AIR | Forced draft fan | SECAIR | Compressor | S-AIR-C | Compressed secondary air |
| 4 | Coal | COALCOMP | Mixing all the boiler inlet streams | BOIL-MX | Mixer | 2-BIOLER | Mixture of coal and air |
|  | Primary compressed air | P-AIR-C |  |  |  |  |  |
|  | Secondary compressed air | S-AIR-C |  |  |  |  |  |
|  | Air leakage | LEAK-AIR |  |  |  |  |  |
| 5 | Mixture of coal and air | 2-BIOLER | Combustion of coal with air producing heat and flue gases | BOILER | RStoic | 2-ASHREM | Flue gas from the bioler |
| 6 | Flue gas from the boiler | 2-ASHREM | Separation of ash from the bioler flue gas | ASHREM | Flash2 | 2-BH | Ash free flue gases from the bioler |
|  |  |  |  |  |  | ASH | Separated ash from the combustion products |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 7 | Ash free flue gases from the bioler | 2-BH | Separation of fly ash from the flue gases of bioler | BAGHSE | Flash2 | 2-PCOMP | Flue gases free from fly ash |
|  |  |  |  |  |  | PARTICLE | Particulate matters |
| 8 | Flue gases free from fly ash | 2-PCOMP | Induced draft fan pulling vacuum on PC boiler | PCOMP | Compressor | 2-FGD | Compressed flue gases free from fly ash |
| 9 | Water for limestone | LIME-H2O | Combining water and limestone to produce slurry stream | LIME-MIX | Mixer | LIM+H2O | Limestone Slurry |
|  | Limestone | RAWLIME |  |  |  |  |  |
| 10 | Limestone Slurry | LIM+H2O | Pumping of the slurry to the FGD mixer | LIM-PUMP | Pump | SLRY2FGD | Limestone slurry |
| 11 | Air for FGD | FGD-AIR | Compression of the air for FGD | FGD-COMP | Compressor | FGD-CAIR | Compressed air for FGD |
| 12 | Compressed flue gases free from fly ash | 2-FGD | Combines all the four streams to be fed to the FGD | FGD-MIX | Mixer | INP-FGD | Inlet stream to FGD |
|  | Compressed air for FGD | FGD-CAIR |  |  |  |  |  |
|  | Water for FGD | H2O-FGD |  |  |  |  |  |
|  | Limestone slurry | SLRY2FGD |  |  |  |  |  |
| 13 | Inlet stream to FGD | INP-FGD | Removal of sulfur from the fule gases of bioler | FGD | RStoic | 2-GYPREM | FGD product stream |
| 14 | FGD product stream | 2-GYPREM | Separation of gypsum from the product of FGD | GYP-REM | Flash2 | 2-SO2REM | Flue gases |
|  |  |  |  |  |  | 2-GYPMIX | Gypsum to be mixed with water |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 15 | Total make-up water | MUP-H2O | Splitting of make-up stream for FGD between gypsum and recycle | GY-FGD-W | Fsplit | GYP-H2O | Water for gypsum |
|  |  |  |  |  |  | FGD-H20 | Water for FGD |
| 16 | Gypsum to be mixed with water | 2-GYPMIX | Addition of make-up water to gypsum product stream | GYP-MIX | Mixer | GYPSUM | Gypsum |
|  | Water | GYP-H2O |  |  |  |  |  |
| STEAM SECTION |  |  |  |  |  |  |  |
| 17 | Inlet feed water | FW-IN | Feed water Heater – liquid side | H8 | Heater | BW-1 | Heated feed water from stage 1 |
| 18 | Heated feed water from stage 1 | BW-1 | Feed water Heater – liquid side | H7 | Heater | BW-4 | Heated feed water from stage 2 |
| 19 | Heated feed water from stage 2 | BW-4 | Feed water Heater – liquid side | H6 | Heater | BW-5 | Heated feed water from stage 3 |
| 20 | Heated feed water from stage 3 | BW-5 | Feed water Heater – liquid side | H5 | Heater | BW-6 | Heated feed water from stage 4 |
| 21 | Drain from stage 3 | DR3 | Deaerator | H4-DEA | Heater | BW-6B | Heated feed water from deaerator |
|  | Extracted steam to feed water heater 4 – steam side | 2-H4 |  |  |  |  |  |
|  | Heated feed water from stage 4 | BW-6 |  |  |  |  |  |
| 22 | Heated feed water from deaerator | BW-6B | Feed water Pump | FW-PUMP | Pump | BW-7 | Heated feed water from feedwater pump |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 23 | Heated feed water from feedwater pump | BW-7 | Feed water Heater – liquid side | H3 | Heater | BW-8 | Heated feed water from stage 6 |
| 24 | Heated feed water from stage 6 | BW-8 | Feed water Heater – liquid side | H2 | Heater | BW-9 | Heated feed water from stage 7 |
| 25 | Heated feed water from stage 7 | BW-9 | Feed water Heater – liquid side | H1 | Heater | FW-OUT | Heated feed water from stage 8 |
| 26 | Heated feed water from stage 8 | FW-OUT | Steam supertheater | SUP-HEAT | Heater | 2-STMLOS | Process steam |
| 27 | Steam | 2-STMLOS | Heat lost in super heater | STM-LOSS | Heater | STEAMOUT | Actual steam after loss |
| 28 | Input steam for turbine | STEAM | Valve stem leakage | V1-LEAK | FSplit | 2-GOV-HP | Steam after the valve stem leakage |
|  |  |  |  |  |  | 2-IPMIX2 | Steam for the IPT from the valve stem leakage |
| 29 | Steam after the valve stem leakage | 2-GOV-HP | Governing stage of HP turbine | GOV-HPT | Compressor | 2-SH1-LK | Steam for shaft 1 |
| 30 | Steam for shaft 1 | 2-SH1-LK | Shaft 1 leakage | SHFT1-LK | FSplit | 2-HPT-1 | Steam from shaft 1 to HPT1 |
|  |  |  |  |  |  | 2-SH1A-L | Steam leakage from shaft 1 |
| 31 | Steam from shaft 1 to HPT1 | 2-HPT-1 | High Pressure Turbine Section 1 | HPT-1 | Compressor | 2-XTR-1 | Steam to extractor 1 |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 32 | Steam to extractor 1 | 2-XTR-1 | Stream extraction for stage 1 | S-XTR-1 | FSplit | 2-VLV-1 | Steam extracted for stage 1 |
|  |  |  |  |  |  | 2-HPT-2 | Steam extracted for HPT2 |
| 33 | Steam extracted for HPT 2 | 2-HPT-2 | High Pressure Turbine Section 2 | HPT-2 | Compressor | 2-SH2-LK | Steam for shaft 2 |
| 34 | Steam for shaft 2 | 2-SH2-LK | Shaft 2 leakage | SHFT2-LK | FSplit | 2-XTR-2 | Steam to extractor 2 |
|  |  |  |  |  |  | 2-SH3-LK | Steam for shaft 3 |
| 35 | Steam to extractor 2 | 2-XTR-2 | Stream extraction for stage 2 | S-XTR-2 | FSplit | 2-VLV-2 | Steam extracted for stage 2 |
|  |  |  |  |  |  | 2-RHT-MX | Steam from extractor 2 to reheater mixer |
| 36 | Steam from extractor 2 to reheater mixer | 2-RHT-MX | Inlet mixer for reheater | RHT-MIX | Mixer | 2-RHT-T | Steam to reheater |
|  | Steam from shaft1a to the reheater | 2-RHT |  |  |  |  |  |
| 37 | Steam to reheater | 2-RHT-T | Steam reheater | RE-HEAT | Heater | 2-RHT-LO | Steam to reheater loss |
| 38 | Steam to reheater loss | 2-RHT-LO | Heat lost from reheater | REHT-LOS | Heater | 2-IPMIX1 | Steam from reheater to IP-MIXER |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 39 | Steam from reheater to IP-MIXER | 2-IPMIX1 | Inlet mixer for IP turbine | IP-MIX | Mixer | 2-MPT1 | Steam extracted for MPT1 |
|  | Steam for the IPT from the valve stem leakage | 2-IPMIX2 |  |  |  |  |  |
| 40 | Steam extracted for MPT1 | 2-MPT1 | Medium Pressure Turbine Section 1 | MPT-1 | Compressor | 2-XTR-3 | Steam to extractor 3 |
| 41 | Steam to extractor 3 | 2-XTR-3 | Stream extraction for stage 3 | S-XTR-3 | FSplit | 2-VLV-3 | Steam extracted for stage 3 |
|  |  |  |  |  |  | 2-MPT2 | Steam extracted for MPT2 |
| 42 | Steam extracted for MPT2 | 2-MPT2 | Medium Pressure Turbine Section 2 | MPT-2 | Compressor | 2-XTR-4 | Steam to extractor 4 |
| 43 | Steam to extractor 4 | 2-XTR-4 | Steam extraction for stage 4 | S-XTR-4 | FSplit | 2-MXR-4 | Steam from MPT to valve 4 |
|  |  |  |  |  |  | 2-SH4-LK | Steam for shaft 4 |
| 44 | Steam for shaft 4 | 2-SH4-LK | Shaft 4 leakage | SHFT4-LK | FSplit | 2-CROOVE | Steam to the cross over valve |
|  |  |  |  |  |  | 2-S4-LK-2 | Steam to SSR mixer |
| 45 | Steam to the cross over valve | 2-CROOVE | Cross over valve for head loss of crossover | CROSSOVER | Valve | 2-LPSPLT | Steam to LP section |
| 46 | Steam to LP section | 2-LPSPLT | Low pressure steam extraction | LP-SPLT | FSplit | 2-LPT-1 | Steam extracted for LPT1 |
|  |  |  |  |  |  | 2-FW-TRB | Steam to feed water turbine |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 47 | Steam extracted for LPT1 | 2-LPT-1 | Low Pressure Turbine Section 1 | LPT-1 | Compressor | 2-XTR-5 | Steam to extractor 5 |
| 48 | Steam to extractor 5 | 2-XTR-5 | Steam extraction for stage 5 | S-XTR-5 | FSplit | 2-LPT-2 | Steam extracted for LPT2 |
|  |  |  |  |  |  | 2-VLV-5 | Steam extracted for stage 5 |
| 49 | Steam extracted for LPT2 | 2-LPT-2 | Low Pressure Turbine Section 2 | LPT-2 | Compressor | 2-XTR-6 | Steam to extractor 6 |
| 50 | Steam to extractor 6 | 2-XTR-6 | Steam extraction for stage 6 | S-XTR-6 | FSplit | 2-LPT-3 | Steam extracted for LPT3 |
|  |  |  |  |  |  | 2-VLV-6 | Steam extracted for stage 6 |
| 51 | Steam extracted for LPT3 | 2-LPT-3 | Low Pressure Turbine Section 3 | LPT-3 | Compressor | 2-XTR-7 | Steam to extractor 7 |
| 52 | Steam to extractor 7 | 2-XTR-7 | Stream extraction for stage 7 | S-XTR-7 | FSplit | 2-MXR-7 | Steam to valve 7 |
|  |  |  |  |  |  | 2-LPT-4 | Steam extracted for LPT4 |
| 53 | Steam extracted for LPT4 | 2-LPT-4 | Low Pressure Turbine Section 4 | LPT-4 | Compressor | 2-XTR-8 | Steam to extractor 8 |
| 54 | Steam to extractor 8 | 2-XTR-8 | Stream extraction for stage 8 | S-XTR-8 | FSplit | 2-VLV-8 | Steam extracted for stage 8 |
|  |  |  |  |  |  | 2-LP-5 | Steam extracted for LPT5 |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 55 | Steam extracted for LPT5 | 2-LP-5 | Low Pressure Turbine Section 5 | LPT-5 | Compressor | LPT-COND | Steam from LPT to condensor |
| 56 | Steam to feed water turbine | 2-FW-TRB | Feed water turbine | FW-TRB | Compressor | MPT-COND | Steam from MPT to condensor |
| 57 | Steam for shaft 3 | 2-SH3-LK | Shaft 3 leakage | SHFT3-LK | Fsplit | 2-MIX-4 | Steam to valve 4 mixer |
|  |  |  |  |  |  | SH3L-SSR | Steam from shaft 3 to SSR |
| 58 | Steam leakage from shaft 1 | 2-SH1A-L | Shaft 1a leakage | SHFT1A-L | Fsplit | 2-RHT | Steam from shaft1a to the reheater |
|  |  |  |  |  |  | 2-SH1B-L | Steam from shaft 1a to valve 4 and SSR |
| 59 | Steam from shaft 1a to valve 4 and SSR | 2-SH1B-L | Shaft 1b leakage | SHFT1B-L | Fsplit | 2-VLV4 | Steam from shaft 1a to valve 4 |
|  |  |  |  |  |  | SH1B-SSR | Steam from shaft 1a to SSR |
| 60 | Steam from shaft 3 to SSR | SH3L-SSR | Mixer for steam seal regulator | SSR-MIXR | Mixer | 2-SSRSP | Steam to SSR |
|  | Steam to SSR mixer | 2-S4-LK2 |  |  |  |  |  |
|  | Steam from shaft 1a to SSR | SH1B-SSR |  |  |  |  |  |
| 61 | Steam to SSR | 2-SSRSP | Steam seal regulator outflow splits | SSR-SPLT | Fsplit | 2-VLV7 | Steam to valve 7 |
|  |  |  |  |  |  | SSR-COND | Steam to condenser |
|  |  |  |  |  |  | 2-SPE | Steam to SPE |
| 62 | Steam to SPE | 2-SPE | Steam packing exhauster – steam side | SPE-STM | Heater | SPE-COND | Steam to condenser |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 63 | Steam from condenser | 2-CN-PUMP | Condensate pump | CON-PUMP | Pump | 2-SPECN | Steam to SPE-condensate side |
| 64 | Steam to SPE-condensate side | 2-SPECN | Steam packing exhauster–condensate side | SPE-COND | Heater | FW-IN | Inlet feed water |
| 65 | Steam extracted for stage 1 | 2-VLV-1 | Head loss in 1st extraction | VALVE-1 | Valve | 2-H1B | Extracted steam to feed water heater 1 – steam side |
| 66 | Steam from LPT to condenser | LPT-COND | Condenser | COND | Heater | 2-CN-PUMP | Steam from condenser |
|  | Steam from MPT to condenser | MPT-COND |  |  |  |  |  |
|  | Steam from SSR to condenser | SSR-COND |  |  |  |  |  |
|  | Steam from SPE to condenser | SPE-COND |  |  |  |  |  |
|  | Make-up water in condenser | MU-COND |  |  |  |  |  |
|  | Steam from feed water heater stage 8 – steam side to condenser | DR8-COND |  |  |  |  |  |
| 67 | Steam extracted for stage 2 | 2-VLV-2 | Head loss in 2nd extraction | VALVE-2 | Valve | 2-H2B | Extracted steam to feed water heater 2 – steam side |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 68 | Steam extracted for stage 3 | 2-VLV-3 | Head loss in 3rd extraction | VALVE-3 | Valve | 2-H3B | Extracted steam to feed water heater 3 – steam side |
| 69 | Steam extracted from stage 4 | 2-MXR-4 | Inlet mixer for valve 4 | VLV-4-MX | Mixer | 2-VLV-4 | Total steam extracted for deaerator |
|  | Steam extracted from shaft 1b | 2-VLV4 |  |  |  |  |  |
|  | Steam extracted from shaft 3 | 2-MIX-4 |  |  |  |  |  |
| 70 | Total steam extracted for deaerator | 2-VLV-4 | Head loss in 4th extraction | VALVE-4 | Valve | 2-H4B | Extracted steam to deaerator |
| 72 | Steam extracted for stage 6 | 2-VLV-6 | Head loss in 6th extraction | VALVE-6 | Valve | 2-H6B | Extracted steam to feed water heater 6 – steam side |
| 73 | Steam extracted from stage 7 | 2-VLV7 | Inlet mixer for valve 7 | VLV-7-MX | Mixer | 2-VLV-7 | Total steam extracted for stage 7 |
|  | Steam extracted from SSR | 2-MXR-7 |  |  |  |  |  |
| 74 | Total steam extracted for stage 7 | 2-VLV-7 | Head loss in 7th extraction | VALVE-7 | Valve | 2-H7B | Extracted steam to feed water heater 7 – steam side |
| 75 | Steam extracted for stage 8 | 2-VLV-8 | Head loss in 8th extraction | VALVE-8 | Valve | 2-H8B | Extracted steam to feed water heater 8 – steam side |
| Sl. No. | INPUT STREAM |  | BLOCK |  |  | OUTPUT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 76 | Extracted steam to feed water heater 8 – steam side | 2-H8B | Feed water Heater – steam side | H8B | Heater | DR8-COND | Steam from feed water heater stage 8 – steam side to condenser |
|  | Drain from stage 7 | DR7 |  |  |  |  |  |
| 77 | Extracted steam to feed water heater 7 – steam side | 2-H7B | Feed water Heater – steam side | H7B | Heater | DR7 | Drain from stage 7 |
|  | Drain from stage 6 | DR6 |  |  |  |  |  |
| 78 | Extracted steam to feed water heater 6 – steam side | 2-H6B | Feed water Heater – steam side | H6B | Heater | DR6 | Drain from stage 6 |
|  | Drain from stage 5 | DR5 |  |  |  |  |  |
| 79 | Extracted steam to feed water heater 5 – steam side | 2-H5B | Feed water Heater – steam side | H5B | Heater | DR5 | Drain from stage 5 |
| 80 | Extracted steam to feed water heater 3 – steam side | 2-H3B | Feed water Heater – steam side | H3B | Heater | DR3 | Drain from stage 3 |
|  | Drain from stage 2 | DR2 |  |  |  |  |  |
| 81 | Extracted steam to feed water heater 2 – steam side | 2-H2B | Feed water Heater – steam side | H2B | Heater | DR2 | Drain from stage 2 |
|  | Drain from stage 1 | DR1 |  |  |  |  |  |
| 82 | Extracted steam to feed water heater 1 – steam side | 2-H1B | Feed water Heater – steam side | H1B | Heater | DR1 | Drain from stage 1 |

Table 2-7
Unit Operations with Energy Streams

| Sl. No. | INPUT HEAT STREAM |  | BLOCK |  |  | OUTPUT HEAT STREAM |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| BOILER SECTION |  |  |  |  |  |  |  |
| 1 | - | - | Decomposition of coal into individual components | DECOM | RYield | Q-DECOMP | Heat released due to the breaking down of coal |
| 2 | Heat released due to the breaking down of coal | Q-DECOMP | Combustion of coal with air producing heat and flue gases | BOILER | RStoic | QBOILER | Heat released from the boiler |
| 3 | - | - | Removal of sulfur from the flue gases of boiler | FGD | RStoic | Q-FGD | Heat released from FGD |
| STEAM SECTION |  |  |  |  |  |  |  |
| 4 | - | - | Feed water Heater – liquid side | H8 | Heater | Q-H8-LS | Heat change in liquid side of stage 8 |
| 5 | - | - | Feed water Heater – liquid side | H7 | Heater | Q-H7-LS | Heat change in liquid side of stage 7 |
| 6 | - | - | Feed water Heater – liquid side | H6 | Heater | Q-H6-LS | Heat change in liquid side of stage 6 |
| 7 | - | - | Feed water Heater – liquid side | H5 | Heater | Q-H5-LS | Heat change in liquid side of stage 5 |
| 8 | - | - | Deaerator | H4-DEA | Heater | Q-DEA | Heat change in the deaerator |
| 9 | - | - | Feed water Heater – liquid side | H3 | Heater | Q-H3-LS | Heat change in liquid side of stage 3 |
| 10 | - | - | Feed water Heater – liquid side | H2 | Heater | Q-H2-LS | Heat change in liquid side of stage 2 |
| Sl. No. | INPUT HEAT STREAM |  | BLOCK |  |  | OUTPUT HEAT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 12 | - | - | Steam supertheater | SUP-HEAT | Heater | Q-SPRHTR | Heat from superheater |
| 13 | - | - | Heat lost in super heater | STM-LOSS | Heater | QSTM-LOS | Heat loss |
| 14 | - | - | Steam reheater | RE-HEAT | Heater | Q-RHT | Heat from the reheater |
| 15 | - | - | Heat lost from reheater | REHT-LOS | Heater | Q-RHT-LO | Heat lost in the reheater |
| 16 | - | - | Steam packing exhauster – steam side | SPE-STM | Heater | Q-SPE-ST | Heat from SPE – steam side |
| 17 | - | - | Condenser | COND | Heater | Q-CONDEN | Heat from the condenser |
| 18 | Heat from SPE – steam side | Q-SPE-ST | Steam packing exhauster - condensate side | SPE-COND | Heater | - | - |
| 19 | - | - | Feed water Heater – steam side | H8B | Heater | Q-H8-SS | Heat change in steam side of stage 8 |
| 20 | - | - | Feed water Heater – steam side | H7B | Heater | Q-H7-SS | Heat change in steam side of stage 7 |
| 21 | - |  | Feed water Heater – steam side | H6B | Heater | Q-H6-SS | Heat change in steam side of stage 6 |
| 22 | - | - | Feed water Heater – steam side | H5B | Heater | Q-H5-SS | Heat change in steam side of stage 5 |
| 23 | - | - | Feed water Heater – steam side | H3B | Heater | Q-H3-SS | Heat change in steam side of stage 3 |
| 24 | - | - | Feed water Heater – steam side | H2B | Heater | Q-H2-SS | Heat change in steam side of stage 2 |
| Sl. No. | INPUT HEAT STREAM |  | BLOCK |  |  | OUTPUT HEAT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 25 | - | - | Feed water Heater – steam side | H1B | Heater | Q-H1-SS | Heat change in steam side of stage 1 |
| 26 | Heat change in steam side of stage 8 | Q-H8-SS | Heat mixer between the steam side heater (H8B) and the heater on feed water side (H8) | Q-MIX-H8 | Heat Mixer | Q-H8 | Net heat change in stage 8 |
|  | Heat change in liquid side of stage 8 | Q-H8-LS |  |  |  |  |  |
| 27 | Heat change in steam side of stage 7 | Q-H7-SS | Heat mixer between the steam side heater (H7B) and the heater on feed water side (H7) | Q-MIX-H7 | Heat Mixer | Q-H7 | Net heat change in stage 7 |
|  | Heat change in liquid side of stage 7 | Q-H7-LS |  |  |  |  |  |
| 28 | Heat change in steam side of stage 6 | Q-H6-SS | Heat mixer between the steam side heater (H6B) and the heater on feed water side (H6) | Q-MIX-H6 | Heat Mixer | Q-H6 | Net heat change in stage6 |
|  | Heat change in liquid side of stage 6 | Q-H6-LS |  |  |  |  |  |
| 29 | Heat change in steam side of stage 5 | Q-H5-SS | Heat mixer between the steam side heater (H5B) and the heater on feed water side (H5) | Q-MIX-H5 | Heat Mixer | Q-H5 | Net heat change in stage 5 |
|  | Heat change in liquid side of stage 5 | Q-H5-LS |  |  |  |  |  |
| Sl. No. | INPUT HEAT STREAM |  | BLOCK |  |  | OUTPUT HEAT STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 30 | Heat change in steam side of stage 3 | Q-H3-SS | Heat mixer between the steam side heater (H3B) and the heater on feed water side (H3) | Q-MIX-H3 | Heat Mixer | Q-H3 | Net heat change in stage 3 |
|  | Heat change in liquid side of stage 3 | Q-H3-LS |  |  |  |  |  |
| 31 | Heat change in steam side of stage 2 | Q-H2-SS | Heat mixer between the steam side heater (H2B) and the heater on feed water side (H2) | Q-MIX-H2 | Heat Mixer | Q-H2 | Net heat change in stage 2 |
|  | Heat change in liquid side of stage 2 | Q-H2-LS |  |  |  |  |  |
| 32 | Heat change in steam side of stage 1 | Q-H1-SS | Heat mixer between the steam side heater (H1B) and the heater on feed water side (H1) | Q-MIX-H1 | Heat Mixer | Q-H1 | Net heat change in stage 1 |
|  | Heat change in liquid side of stage 1 | Q-H1-LS |  |  |  |  |  |
| 33 | Heat released from the boiler | QBOILER | Modeling heat loss in the boiler | BOIL-LOS | Heat Splitter | Q-BI-LOS | Heat lost in boiler |
|  |  |  |  |  |  | QSTEAM | Heat to generate steam |
| 34 | Heat to generate steam | QSTEAM | Using heat from the boiler to heat the feedwater | QMIX-BLR | Heat Mixer | Q-EFF | Heat difference between the heat from the boiler and the heat for the steam cycle |
|  | Total heat from superheater and reheater | Q-STMTOT |  |  |  |  |  |
| 35 | Heat from superheater | Q-SPRHTR | Mixing the heat from superheater and reheater | QMIX-STM | Heat Mixer | Q-STMTOT | Total heat from superheater and reheater |
|  | Heat from reheater | Q-RHT |  |  |  |  |  |

Table 2-8
Unit Operations with Work Streams

| Sl. No. | INPUT WORK STREAM |  | BLOCK |  |  | OUTPUT WORK STREAM |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| BOILER SECTION |  |  |  |  |  |  |  |
| 1 | - | - | Primary air compression | PRIAIR | Compressor | W-PA-FAN | Work from primary air compressor |
| 2 | - | - | Forced draft fan | SECAIR | Compressor | W-SA-FAN | Work from secondary air compressor |
| 3 | - | - | Induced draft fan pulling vacuum on PC boiler | PCOMP | Compressor | W-PCOMP | Work from induced draft fan |
| STEAM SECTION |  |  |  |  |  |  |  |
| 4 | - | - | Feed water Pump | FW-PUMP | Pump | W-FW-PUM | Work from feedwater pump |
| 5 | - | - | Governing stage of HP turbine | GOV-HPT | Compressor | W-LP-5 | Work from GOV-HPT |
| 6 | - | - | High Pressure Turbine Section 1 | HPT-1 | Compressor | W-HP-1 | Work from HPT-1 |
| 7 | - | - | High Pressure Turbine Section 2 | HPT-2 | Compressor | W-HP-2 | Work from HPT-2 |
| 8 | - | - | Medium Pressure Turbine Section 1 | MPT-1 | Compressor | W-IP-2 | Work from MPT-1 |
| 9 | - | - | Medium Pressure Turbine Section 2 | MPT-2 | Compressor | W-IP-1 | Work from MPT-2 |
| 10 | - | - | Low Pressure Turbine Section 1 | LPT-1 | Compressor | W-LP-1 | Work from LPT-1 |
| Sl. No. | INPUT WORK STREAM |  | BLOCK |  |  | OUTPUT WORK STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 11 | - | - | Low Pressure Turbine Section 2 | LPT-2 | Compressor | W-LP-2 | Work from LPT-2 |
| 12 | - | - | Low Pressure Turbine Section 3 | LPT-3 | Compressor | W-LP-3 | Work from LPT-3 |
| 13 | - | - | Low Pressure Turbine Section 4 | LPT-4 | Compressor | W-LP-4 | Work from LPT-4 |
| 14 | - | - | Low Pressure Turbine Section 5 | LPT-5 | Compressor | W-LP-5 | Work from LPT-5 |
| 15 | Turbine loss | W-TURLOS | Work mixer | W-SUMMER | Mixer | W-TOTAL | Total work form all the turbines after turbine loss |
|  | Work from LPT-5 | W-LP-5 |  |  |  |  |  |
|  | Work from LPT-4 | W-LP-4 |  |  |  |  |  |
|  | Work from LPT-3 | W-LP-3 |  |  |  |  |  |
|  | Work from LPT-2 | W-LP-2 |  |  |  |  |  |
|  | Work from LPT-1 | W-LP-1 |  |  |  |  |  |
|  | Work from MPT-2 | W-IP-2 |  |  |  |  |  |
|  | Work from MPT-1 | W-IP-1 |  |  |  |  |  |
|  | Work from GOV-HPT | W-HPGOV |  |  |  |  |  |
|  | Work from HPT-2 | W-HP-2 |  |  |  |  |  |
|  | Work from HPT-1 | W-HP-1 |  |  |  |  |  |
| Sl. No. | INPUT WORK STREAM |  | BLOCK |  |  | OUTPUT WORK STREAM |  |
|  | Stream | ASPEN ID | Process | ASPEN ID | ASPEN UNIT | ASPEN ID | Stream |
| 16 | - | - | Feed water turbine | FW-TRB | Compressor | W-FW-TRB | Work from feedwater turbine |
| 17 | - | - | Condensate Pump | CON-PUMP | Pump | W-CON-PM | Work from the condensate pump |
| 18 | Total work form all the turbines after turbine loss | W-TOTAL | To model the work loss | WORKLOSS | Splitter | W-USE | Usefulwork |
| 19 | Work from feedwater turbine | W-FW-TRB | Work mixer from feedwater pump and feedwater turbine | WPU+WTRB | Mixer | W-FW | Work from feedwater |
|  | Work from feedwater pump | W-FW-PUM |  |  |  |  |  |

ASPEN Design Specification & Convergence Blocks

The following section is a brief description on the convergence blocks from ASPEN. Additional details can be obtained from ASPEN Plus manuals or ASPEN help section. A design specification sets the value of a variable that ASEPN would otherwise calculate. For each design specification, a block input variable, process feed stream variable, or other simulation input to be manipulated (adjusted) is identified to meet the specification. When a design specification is used, a desired value for a flowsheet variable or some function of flowsheet variables is specified. The flowsheet variables used in a design specification are called sampled variables. For each design specification, a block input variable or process feed stream variable to be adjusted to satisfy the design specification is also selected. This variable is called the manipulated variable.

The design specification achieves its objective by manipulating an input variable specified by the user. A single design specification can only manipulate the value of one input variable. Design specifications create loops that must be solved iteratively. The value of the manipulated variable that is provided in the Stream or Block input is used as the initial estimate and hence providing a good estimate for the manipulated variable will help the design specification to converge in fewer iterations. This is especially important for large flowsheets with several interrelated design specifications.

The objective of the specification is that it equals the calculated value. The specification can be any valid Fortran expression involving one or more flowsheet quantities. Specifications must also have a tolerance within which the objective function relation must be satisfied. Therefore, the actual equation that must be satisfied is

| Specified Value - Calculated Value | < Tolerance

This coal power plant model in ASPEN uses 15 design specification blocks. A detailed list of these convergence blocks along with their purpose, range and tolerance is given in Table 2-10. A convergence block is associated with each of the design specifications. The list of these convergence blocks is presented in Table 2-10.

Table 2-9
List of Design Sepcifications

| Sl. No. | ASPEN ID | Purpose | ASPEN Input | ASPEN Manipulated Variable | Range | Target | Tolerance |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | D-BFW | Extract sufficient steam to match the work requirements of feed water pump by the work produced by the boiler feed water turbine | WORK-POWER of the Stream W-FW-TRB and WORK-POWER of the Stream W-FW-PUM | FLOW/FRAC of the Stream 2-FW-TRB of the Block LP-SPLT | 200000 500000 | WORK-POWER of the Stream W-FW-TRB should be equal to the negative of WORK-POWER of the Stream W-FW-TRB | 100.0 |
| 2 | D-FGD-O2 | Determine the oxidation air requirements by FGD | MOLE-FLOW of the O2 component of the Stream FGD-AIR MOLE-FLOW of the O2S component of the Stream 2-FGD | MASS-FLOW of the Stream FGD-AIR | 1000 1000000 | Ratio of mole-flow of O2 and O2S should be 1.1 | 0.02 |
| 3 | D-FGDLIM | Determine the amount of limestone required for the FGD | MOLE-FLOW of the component CACO3 of the Stream LIM+H2O MOLE-FLOW of the component O2S of the Stream INP-FGD | MASS-FLOW of the Steam RAWLIME | 100 100000 | Ratio of mole-flow of CACO3 and O2S should be 1.04 | 0.01 |
| 4 | D-FGDTEM | Determine the amount of water required to maintain an adiabatic FGD | HEAT-DUTY of the stream Q-FGD | MASS-FLOW of the Stream H2O-FGD | 10000 1000000 | HEAT-DUTY of the stream Q-FGD should be zero | 100 |
| Sl. No. | ASPEN ID | Purpose | ASPEN Input | ASPEN Manipulated Variable | Range | Target | Tolerance |
| 5 | D-H1 | Determines the steam to be extracted for stage 1 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H1A HEAT-DUTY of the Stream Q-H1B | FLOW/FRAC of the Stream 2-VLV-1 of the Block S-XTR-1 | 250000 500000 | HEAT-DUTY of the Stream Q-H1A should be equal to the negative of HEAT-DUTY of the Stream Q-H1B | 50 |
| 6 | D-FGDSOL | Determine the amount of water required to create a 30% limestone slurry for the FGD | MASS-FLOW of the Stream RAWLIME MASS-FLOW of the Stream LIM+H2O (Substream MIXED) MASS-FLOW of the Stream LIM+H2O (Substream CISOLID) | MASS-FLOW of the Stream LIME-H2O | 100 1000000 | The ratio of mass flow rates of the RAWLIME Stream to the sum of the mass flow rates of the CISOLID and MIXED substreams of the Stream LIM+H2O should be 0.3 | 0.01 |
| 7 | D-H2 | Determines the steam to be extracted for stage 2 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H2A HEAT-DUTY of the Stream Q-H2B | FLOW/FRAC of the Stream 2-VLV-2 of the Block S-XTR-2 | 10000 1000000 | HEAT-DUTY of the Stream Q-H2A should be equal to the negative of HEAT-DUTY of the Stream Q-H2B | 50 |
| 8 | D-H3 | Determines the steam to be extracted for stage 3 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H2A HEAT-DUTY of the Stream Q-H2B | FLOW/FRAC of the Stream 2-VLV-3 of the Block S-XTR-3 | 10000 1000000 | HEAT-DUTY of the Stream Q-H3A should be equal to the negative of HEAT-DUTY of the Stream Q-H3B | 50 |
| 9 | D-H4 | Determines the steam to be extracted for stage 4 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H4A | FLOW/FRAC of the Stream 2-MXR-4 of the Block S-XTR-4 | 50000.0 200000.0 | FLOW/FRAC of the Stream 2-MXR-4 of the Block S-XTR-4 should be equal to zero | 100 |
| Sl. No. | ASPEN ID | Purpose | ASPEN Input | ASPEN Manipulated Variable | Range | Target | Tolerance |
| 10 | D-H5 | Determines the steam to be extracted for stage 5 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H5A HEAT-DUTY of the Stream Q-H5B | FLOW/FRAC of the Stream 2-VLV-5 of the Block S-XTR-5 | 100 5000000 | HEAT-DUTY of the Stream Q-H5A should be equal to the negative of HEAT-DUTY of the Stream Q-H5B | 50 |
| 11 | D-H6 | Determines the steam to be extracted for stage 6 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H6A HEAT-DUTY of the Stream Q-H6B | FLOW/FRAC of the Stream 2-VLV-6 of the Block S-XTR-6 | 70000 200000 | HEAT-DUTY of the Stream Q-H6A should be equal to the negative of HEAT-DUTY of the Stream Q-H6B | 50 |
| 12 | D-H7 | Determines the steam to be extracted for stage 3 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H7A HEAT-DUTY of the Stream Q-H7B | FLOW/FRAC of the Stream 2-VLV-7 of the Block S-XTR-7 | 60000 200000 | HEAT-DUTY of the Stream Q-H7A should be equal to the negative of HEAT-DUTY of the Stream Q-H7B | 600.0 |
| 13 | D-H8 | Determines the steam to be extracted for stage 8 so as to maintain an adiabatic feedwater heather | HEAT-DUTY of the Stream Q-H8A HEAT-DUTY of the Stream Q-H8B | FLOW/FRAC of the Stream 2-VLV-8 of the Block S-XTR-8 | 50000 370000 | HEAT-DUTY of the Stream Q-H8A should be equal to the negative of HEAT-DUTY of the Stream Q-H8B | 1000.0 |
| 14 | D-PWROUT | Determine the flowrate of the steam to generate the specified amount of power | WORK-POWER of the Stream W-USE | MASS-FLOW of the Stream STEAM | 3000000 6000000 | WORK-POWER of the Stream W-USE should be equal to -898400 | 50 |
| 15 | D-ST-COA | Determine the flowrate of coal that will be required so that the boiler heat duty is equal to that of the steam requirement | HEAT-DUTY of the Stream QSTEAM HEAT-DUTY of the Stream QSTMTOT | MASS-FLOW of the Stream COAL | 3000000 6000000 | HEAT-DUTY of the Stream QSTEAM should be equal to the negative of the HEAT-DUTY of the stream QSTMTOT | 1000 |

Table 2-10
List of Convergences

| Sl. No. | Convergence | Design Specification | Type |
| --- | --- | --- | --- |
| 1 | CO-BFW | D-BFW | BROYDEN |
| 2 | CO-FGD-O | D-FGD-O2 | BROYDEN |
| 3 | CO-FGDLI | D-FGDLIM | BROYDEN |
| 4 | CO-FGDSO | D-FGDSOL | BROYDEN |
| 5 | CO-FGDTE | D-FGDTEM | BROYDEN |
| 6 | CO-H1 | D-H1 | BROYDEN |
| 7 | CO-H2 | D-H2 | BROYDEN |
| 8 | CO-H3 | D-H3 | BROYDEN |
| 9 | CO-H4 | D-H4 | BROYDEN |
| 10 | CO-H5 | D-H5 | BROYDEN |
| 11 | CO-H6 | D-H6 | BROYDEN |
| 12 | CO-H7 | D-H7 | BROYDEN |
| 13 | CO-H8 | D-H8 | BROYDEN |
| 14 | CO-PWROU | D-PWROUT | BROYDEN |
| 15 | CO-ST-CO | D-ST-COA | BROYDEN |

ASPEN Calculator Blocks

ASPEN provides Calculator blocks which allow to use Fortran statements or Excel spreadsheets into flowsheet computations to perform user-defined tasks. These calculator blocks can be used if a direct relationship is known between a process constraint and its associated process variables. This ASPEN model utilizes these calculator blocks to manipulate the process simulation. These calculators could have been replaced by design specifications but such a strategy would have resulted in a longer convergence time as it would require additional computational time for unnecessary design specification iterations. The present ASPEN Plus based coal power plant model uses a total of 19 calculator blocks as shown in Table 2-11. This table also shows the purpose of each of these calculators. The table also consists of the process variable determined by each of these calculators along with the required input for them.

Since ASPEN is a sequential modular simulator that executes one unit operation at a time, it is imperative to specify where in the sequence of unit operations each Calculator block is to be executed. This detail is also presented in Table 2-11.

Table 2-11
List of Calculators

| Sl. No. | Name | Purpose | ASPEN Inputs | ASPEN Output | Sequence |
| --- | --- | --- | --- | --- | --- |
| 1 | C-H1 | Determines the outlet temperature of the feed water from the liquid side feed water heater 1 | TDEW of Stream 2-H1B | TEMP of Block H1 | Before unit operation H1 |
| 2 | C-H1B | Determines the outlet temperature of the drain from the steam side feed water heater 1 | TEMP of Stream BW-9 | TEMP of Block H1B | Before unit operation H1B |
| 3 | C-H2 | Determines the outlet temperature of the feed water from the liquid side feed water heater 2 | TDEW of Stream 2-H2B | TEMP of Block H2 | Before unit operation H2 |
| 4 | C-H2B | Determines the outlet temperature of the drain from the steam side feed water heater 2 | TEMP of Stream BW-8 | TEMP of Block H2B | Before unit operation H2B |
| 5 | C-H3 | Determines the outlet temperature of the feed water from the liquid side feed water heater 3 | TDEW of Stream 2-H3B | TEMP of Block H3 | Before unit operation H3 |
| 6 | C-H3B | Determines the outlet temperature of the drain from the steam side feed water heater 3 | TEMP of Stream BW-7 | TEMP of Block H3B | Before unit operation H3B |
| 7 | C-H4 | Determines the outlet temperature of the feed water from deaerator | TDEW of Stream 2-H4BB | TEMP of Block H4-DEA | Before unit operation H4 |
| 8 | C-H5 | Determines the outlet temperature of the feed water from the liquid side feed water heater 5 | TDEW of Stream 2-H5B | TEMP of Block H5 | Before unit operation H5 |
| 9 | C-H5B | Determines the outlet temperature of the drain from the steam side feed water heater 5 | TEMP of Stream BW-5 | TEMP of Block H5B | Before unit operation H5B |
| 10 | C-H6 | Determines the outlet temperature of the feed water from the liquid side feed water heater 6 | TDEW of Stream 2-H6B | TEMP of Block H6 | Before unit operation H6 |
| Sl. No. | Name | Purpose | ASPEN Inputs | ASPEN Output | Sequence |
| 11 | C-H6B | Determines the outlet temperature of the drain from the steam side feed water heater 6 | TEMP of Stream BW-4 | TEMP of Block H6B | Before unit operation H6B |
| 12 | C-H7 | Determines the outlet temperature of the feed water from the liquid side feed water heater 7 | TDEW of Stream 2-H7B | TEMP of Block H7 | Before unit operation H7 |
| 13 | C-H7B | Determines the outlet temperature of the drain from the steam side feed water heater 7 | TEMP of Stream BW-1 | TEMP of Block H7B | Before unit operation H7B |
| 14 | C-H8 | Determines the outlet temperature of the feed water from the liquid side feed water heater 8 | TDEW of Stream 2-H8B | TEMP of Block H8 | Before unit operation H8 |
| 15 | C-H8B | Determines the outlet temperature of the drain from the steam side feed water heater 8 | TEMP of Stream FW-IN | TEMP of Block H8B | Before unit operation H8B |
| 16 | C-AIR-IN | Determines the theoretical air requirement depending upon the amount of coal | MASSFLOW of the C,S,H2,O2 in the Stream COALCHEM | MASSFLOW of Stream P-AIR | Before unit operation PRIAIR |
|  |  |  |  | MASSFLOW of Stream S-AIR |  |
|  |  |  |  | MASSFLOW of Stream LEAK-AIR |  |
| 17 | C-DECOMP | Decomposes coal into its individual components | ULTANAL PROXANAL | MASSYIELD of H20,ASH, C,H2,N2,S,O2 in the Block DECOM | Before unit operation DECOM |
| 18 | C-FGDWAT | Determined the make-up water for the FGD unit | MASSFLOW of the Stream 2-GYPMIX MASSFLOW of the Stream 2-GYPMIX MASSFLOW of H20 in the Stream H20-FGD | FLOW/FRAC of the Block GY-FGD-W for the Stream GYP-H20 MASSFLOW of the Stream MUP-H20 | Before unit operation GY-FGD-W |
| 19 | C-BI-LOS | Determines the loss of heat in the boiler | - | FLOW/FRAC of the Stream Q-BI-LOSS in the Block BOIL-LOS | Before the unit operation BOIL-LOS |

ASPEN Computational Sequence

ASEPN is designed to assign flowsheet sequences based on its mathematical derivation of an “optimal” computational sequence. However at times, ASPEN adopts default sequences that result in long convergence times and even diverging simulations. For complex simulations, a user-defined computational sequence can result in a simulation that converges faster. A user-defined computational sequence is also easier to troubleshoot during creation/manipulation, since it is not subject to the varying default sequences ASPEN creates as the model is manipulated. Table 2-12 and Table 2-13show the sequencing used here.

Table 2-12
Sequencing of the Boiler Section

| Sl. No. | Loop-Return | Block Type | Block | Sl. No. | Loop-Return | Block Type | Block |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | UNIT OPERATION | DECOM | 14 |  | UNIT OPERATION | LIME-MIX |
| 2 |  | CALCULATOR | C-AIR-IN | 15 |  | UNIT OPERATION | LIM-PUMP |
| 3 |  | UNIT OPERATION | PRIAIR | 16 |  | UNIT OPERATION | FGD-COMP |
| 4 |  | UNIT OPERATION | SECAIR | 17 | RETURNTO | CONVERGENCE | CO-FGDSO |
| 5 |  | UNIT OPERATION | BOIL-MX | 18 | BEGIN | CONVERGENCE | CO-FGD-O |
| 6 |  | UNIT OPERATION | BOILER | 19 |  | UNIT OPERATION | FGD-MIX |
| 7 |  | UNIT OPERATION | BOIL-LOS | 20 | RETURNTO | CONVERGENCE | CO-FGD-O |
| 8 |  | UNIT OPERATION | ASHREM | 21 | RETURNTO | CONVERGENCE | CO-FGDLI |
| 9 |  | UNIT OPERATION | BAGHSE | 22 |  | UNIT OPERATION | FGD |
| 10 |  | UNIT OPERATION | PCOMP | 23 | RETURNTO | CONVERGENCE | CO-FGDTE |
| 11 | BEGIN | CONVERGENCE | CO-FGDTE | 24 |  | UNIT OPERATION | GYP-REM |
| 12 | BEGIN | CONVERGENCE | CO-FGDLI | 25 |  | CALCULATOR | C-FGDWAT |
| 13 | BEGIN | CONVERGENCE | CO-FGDSO | 26 |  | UNIT OPERATION | GY-FGD-W |
|  |  |  |  | 27 |  | UNIT OPERATION | GYP-MIX |

Table 2-13
Sequencing of the Steam Cycle Section

| Sl. No. | Loop-Return | Block Type | Block | Sl. No. | Loop-Return | Block Type | Block |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | BEGIN | CONVERGENCE | CO-PWROU | 18 |  | UNIT OPERATION | HPT-2 |
| 2 | BEGIN | CONVERGENCE | CO-H1 | 19 |  | UNIT OPERATION | SHFT2-LK |
| 3 | BEGIN | CONVERGENCE | CO-H2 | 20 |  | UNIT OPERATION | SHFT3-LK |
| 4 | BEGIN | CONVERGENCE | CO-H3 | 21 |  | UNIT OPERATION | S-XTR-2 |
| 5 | BEGIN | CONVERGENCE | CO-H4 | 22 |  | UNIT OPERATION | VALVE-2 |
| 6 | BEGIN | CONVERGENCE | CO-H5 | 23 |  | UNIT OPERATION | RHT-MIX |
| 7 | BEGIN | CONVERGENCE | CO-H6 | 24 |  | UNIT OPERATION | RE-HEAT |
| 8 | BEGIN | CONVERGENCE | CO-H7 | 25 |  | UNIT OPERATION | REHT-LOS |
| 9 | BEGIN | CONVERGENCE | CO-H8 | 26 |  | UNIT OPERATION | IP-MIX |
| 10 |  | UNIT OPERATION | V1-LEAK | 27 |  | UNIT OPERATION | MPT-1 |
| 11 |  | UNIT OPERATION | GOV-HPT | 28 |  | UNIT OPERATION | S-XTR-3 |
| 12 |  | UNIT OPERATION | SHFT1-LK | 29 |  | UNIT OPERATION | VALVE-3 |
| 13 |  | UNIT OPERATION | SHFT1A-L | 30 |  | UNIT OPERATION | MPT-2 |
| 14 |  | UNIT OPERATION | SHFT1B-L | 31 |  | UNIT OPERATION | S-XTR-4 |
| 15 |  | UNIT OPERATION | HPT-1 | 32 |  | UNIT OPERATION | VLV-4-MX |
| 16 |  | UNIT OPERATION | S-XTR-1 | 33 |  | UNIT OPERATION | VALVE-4 |
| 17 |  | UNIT OPERATION | VALVE-1 | 34 |  | UNIT OPERATION | SHFT4-LK |
| 35 |  | UNIT OPERATION | SSR-MIXR | 55 |  | UNIT OPERATION | COND |
| Sl. No. | Loop-Return | Block Type | Block | Sl. No. | Loop-Return | Block Type | Block |
| 36 |  | UNIT OPERATION | SSR-SPLT | 56 |  | UNIT OPERATION | CON-PUMP |
| 37 |  | UNIT OPERATION | SPE-STM | 57 |  | UNIT OPERATION | SPE-COND |
| 38 |  | UNIT OPERATION | CROSOVER | 58 |  | UNIT OPERATION | H8 |
| 39 |  | UNIT OPERATION | LP-SPLT | 59 |  | UNIT OPERATION | H7 |
| 40 |  | UNIT OPERATION | FW-TRB | 60 |  | UNIT OPERATION | H6 |
| 41 |  | UNIT OPERATION | LPT-1 | 61 |  | UNIT OPERATION | H5 |
| 42 |  | UNIT OPERATION | S-XTR-5 | 62 |  | UNIT OPERATION | H4-DEA |
| 43 |  | UNIT OPERATION | VALVE-5 | 63 |  | UNIT OPERATION | FW-PUMP |
| 44 |  | UNIT OPERATION | LPT-2 | 64 |  | UNIT OPERATION | H4-DEA |
| 45 |  | UNIT OPERATION | S-XTR-6 | 65 |  | UNIT OPERATION | H3 |
| 46 |  | UNIT OPERATION | VALVE-6 | 66 |  | UNIT OPERATION | H2 |
| 47 |  | UNIT OPERATION | LPT-3 | 67 |  | UNIT OPERATION | H1 |
| 48 |  | UNIT OPERATION | S-XTR-7 | 68 |  | UNIT OPERATION | H1B |
| 49 |  | UNIT OPERATION | VLV-7-MX | 69 |  | UNIT OPERATION | Q-MIX-H1 |
| 50 |  | UNIT OPERATION | VALVE-7 | 70 |  | UNIT OPERATION | H2B |
| 51 |  | UNIT OPERATION | LPT-4 | 71 |  | UNIT OPERATION | Q-MIX-H2 |
| 52 |  | UNIT OPERATION | S-XTR-8 | 72 |  | UNIT OPERATION | H3B |
| 53 |  | UNIT OPERATION | VALVE-8 | 73 |  | UNIT OPERATION | Q-MIX-H3 |
| 54 |  | UNIT OPERATION | LPT-5 | 74 |  | UNIT OPERATION | H5B |
| Sl. No. | Loop-Return | Block Type | Block | Sl. No. | Loop-Return | Block Type | Block |
| 75 |  | UNIT OPERATION | Q-MIX-H5 | 86 | RETURNTO | CONVERGENCE | CO-H4 |
| 76 |  | UNIT OPERATION | H6B | 87 | RETURNTO | CONVERGENCE | CO-H3 |
| 77 |  | UNIT OPERATION | Q-MIX-H6 | 88 | RETURNTO | CONVERGENCE | CO-H2 |
| 78 |  | UNIT OPERATION | H7B | 89 | RETURNTO | CONVERGENCE | CO-H1 |
| 79 |  | UNIT OPERATION | Q-MIX-H7 | 90 |  | UNIT OPERATION | SUP-HEAT |
| 80 |  | UNIT OPERATION | H8B | 91 |  | UNIT OPERATION | STM-LOSS |
| 81 |  | UNIT OPERATION | Q-MIX-H8 | 92 |  | UNIT OPERATION | W-SUMMER |
| 82 | RETURNTO | CONVERGENCE | CO-H8 | 93 |  | UNIT OPERATION | WORKLOSS |
| 83 | RETURNTO | CONVERGENCE | CO-H7 | 94 |  | UNIT OPERATION | QMIX-STM |
| 84 | RETURNTO | CONVERGENCE | CO-H6 | 95 | RETURNTO | CONVERGENCE | CO-PWROU |
| 85 | RETURNTO | CONVERGENCE | CO-H5 | 96 |  | SEQUENCE | BOILER |
|  |  |  |  | 97 |  | UNIT OPERATION | QMIX-BLR |

Summary

In this report, a detailed description of an ASPEN model of a pulverized coal based power plant is developed. Table 2-14 shows a summary of the many components of the ASPEN model.

Table 2-14
Summary of the ASPEN model

| Sl. No | Units | Number of units |
| --- | --- | --- |
| 1 | Sections | 2 |
|  | Boiler Section |  |
|  | Steam Cycle Section |  |
| 2 | Total Streams | 171 |
|  | Mass Streams | 115 |
|  | Energy Streams | 35 |
|  | Work Streams | 21 |
| 3 | Total ASPEN Blocks | 95 |
|  | Unit Operations | 82 |
|  | Heat Mixers/Splitters | 10 |
|  | Work Mixers/Splitters | 3 |
| 4 | Calculator Blocks | 19 |
| 5 | Design Specifications | 15 |
| 6 | Convergence Blocks | 15 |

This model can be further enhanced by adding environmental control technologies, and can also improve the efficiency of the power plant by efficient heat integration between the different parts of the power plant.  The Mercury produced from coal is available in FORT.100 file.

# Summary

This report discusses the model development of a pulverized coal based power plant. The process is modeled based on the usage of atmospheric air for the combustion of pulverized coal to produce a super critical steam which is subsequently used for the production of power. Steam produced by heating the feedwater with the help of combustion heat is extracted from various vantage locations to heat the feed water to be used for the production of steam. Such a strategy leads to an efficient heat integrated system and minimizes the consumption of natural resources. The model has been developed in the ASPEN simulation environment and has 82 unit operations.

References

1.	http://www.worldcoal.org/coal/uses-of-coal/coal-electricity/. Last Accessed: September 2015.

2.	http://en.wikipedia.org/wiki/Coal. Last Accessed: Sep. 2015.

3.	DOE/NETL. (2007c). Cost and performance baseline for fossil energy plants.