## Slide 1: Integrated PC power plant
Modified from “Cost and Performance Baseline for Fossil Energy Plants Volume 1: Bituminous Coal and Natural Gas to Electricity” – NETL REPORT – 2007/1281
BOILER
CC
STEAM CYCLE
Notes: <number>

## Slide 2: Boiler Section
Modeled with 14 ASPEN Blocks
Boiler
  Modeled as RSTOIC - A DECOMP block is also included
  Fuel - Illinois # 6 Coal - 75.21 kg/sec - Oxidant – Air – 796 kg/sec
  Boiler Pressure /Temperature – 14.01psia/270 F
Ash Remover
  Modeled as Flash Drum
  Removes 20% of solid ash in the feed - Added to model the removal of ash from the boiler
Bag House
  Modeled as Flash Drum - Removes remaining ash & particulates in the stream
  Pressure drop of ~0.2 psi
Notes: <number>

## Slide 3: Boiler Section
Flue Gas Desulfurization unit - FGD
  Modeled as an RSTOIC
  O2/SO2 ratio to 1.1 ; CaCO3/SO2 ratio to 1.04 ; slurry mixture is set at 30% solids – design Specifications
  98% of the SO2 is reacted to form CO2 and gypsum
Gypsum Remover
  Modeled as a flash drum
  To model the removal of gypsum, MgCO3, CaCO3, and inert materials from the FGD outlet stream
Flue Gas splitter
  Splits the flue gas into five equal streams to be fed to the Carbon capture system
Notes: <number>

## Slide 4: Steam Section
Steam Cycle – Super Critical
  Pressure - 3514.7 psi
  Temperature – 1110 F
Steam Turbine – Three Sections –
  High Pressure - 3514.7 psi/1110 °F
  Intermediate Pressure - 654 psig/1150°F.
  Low Pressure - 138 psig/717°F
Steam condensed & recycled as Feed Water
Feed water heating
  Seven feed water heaters & a deaerator
Notes: <number>

## Slide 5: Mercury from Coal
Calculator block Mercury
  0.21 mg/kg of coal
  Results in Fort.100
Notes: <number>